MDU-14-SEQ

Specification for Sequential power up/down MDU.

#### Features

Inlet options					Neutrik powerconn

Hardwired

IEC320

Power Switch					Single illuminated rocker  (non load bearing)

Or less power switch version (sequence power up only)

Number of outlets				14

Fuse status indicators				14 x High intensity Green LED

Outlet fuse type					T5A HBC 20mm ceramic

# Remote control & sequence link

# Option

Remote power up input				240VAC @ 7.5mA

Connector type					male

Note: power switch can overide remote control

Sequence link output	240VAC  protected by internal 250mA fuse

Connector type	female

Maximum no. of units that can be linked	Unlimited

# Low voltage remote control

# Options

Remote power up input	5VDC @ 91mA,

12VDC @ 34mA,

24VDC @ 17mA,

or 115VAC @ 14mA

Connector type	male

Note: power switch can overide remote control

#### Specification

### Outlet switching devices

Logic operating voltage				240VAC

Device type					240VAC coil DPDT relays

Contact rating					8A per contact

Maximum turn-on time				12mS

Maximum turn-off time				8mS

Coil resistance					32,500 Ohms

Operating temperature range			-40 deg C to +85 deg C

Neutral switch contact rating			32A

### Overall

Maximum power up sequence time		168mS

Power up spacing				12mS

Power up order					1 to 14

Maximum power down sequence time		112mS

Power down spacing				8mS

Power down order				1 to 14

Operating Voltage range			240VAC version (216VAC to 264VAC)

120VAC version (90VAC to 132VAC)

Operating temperature range			-20 deg C to +75 deg C

Maximum load (power switch version)		16A RMS

Maximum load (no power switch version)	20A RMS

Depth including tie bar				255mm approx

Depth excluding tie bar				160mm approx.

Width						438mm (19 Inch)

Height						44.5mm (1U Rack-mount)

Weight						2Kg approx.

### Performance

The MDU-14-SEQ provides a solution to high switch on/off surge currents. The non load bearing power switch ensures reliable operation over life time of product. Remote power up & sequence link options make this unit highly flexible for many power management systems.

One-4-Power Ltd.

No. 2 Sorrel Close

Burghfield Common

Reading

Berkshire

RG7 3YS

Tel: 0118 9835498

FAX: 0118 9835498

www.one4power.co.uk

email: sales@one4power.co.uk