MDU-14-AS

Specification for Auto Switch MDU.

#### Features

Inlet options					2 x Neutrik powerconn

or 2 x Hardwired

Power Switch					Single illuminated rocker only

or Less switch version

Number of outlets				14

Status Indicators

Power Present inlet 1 (Main)			Green LED

Inlet 1 (Main) selected				Green LED

Power Present inlet 2 (Backup)			Red LED

Inlet 2 (Backup) selected			Red LED

Priority to inlet 1 (Main) – Auto reset		Green LED

Controls

Manual reset to inlet 1 (main)			momentary pushbutton – front panel location

Manual / Auto reset selection	Latching pushbutton – front panel location – access through hole!

Test (force selection of inlet 2 backup)	Momentary pushbutton – front panel location – access through hole!

Remote Control & Alarm fail output

Connector type					9 way “D” Female on flying lead - via rear panel

Inlet 1 (Main) fail				isolated relay contacts N/O & N/C & COM

Inlet 2 (Backup) fail				isolated relay contacts N/O & N/C & COM

Remote reset control	Momentary 12 VDC input 20mA – reverse polarity protected

#### Specification

### Change over switch

Type						High power Solid State relay DPCO

Maximum current rating				50A RMS

Maximum peak current				850Apk  (16.6mS)

810Apk  (20mS)

Maximum voltage rating				480VAC

Transient over voltage				1200Vpk

Maximum turn-on time				20mS  Zero voltage sensing to minimise EMI/RFI

Maximum turn-off time				50mS  Zero current sensing to minimise EMI/RFI

Transient Protection				Output Snubber  circuit

Maximum on state voltage drop			3.4V total

Maximum off state leakage current		1mA

Minimum load current				Any

Operating temperature range			-40 deg C to +80 deg C

### Control Logic

Logic operating voltage				240VAC

Device type					240VAC coil DPDT relays

Error/false state protection			anti – overlap blocking

Maximum turn-on time				12mS

Maximum turn-off time				8mS

Coil resistance					32,500 Ohms

Operating temperature range			-40 deg C to +85 deg C

Operation mode 1				First come – first served (manual reset)

Forced reset when first powered up

Operation mode 2				Priority to inlet 1 – main (auto reset)

### Overall

Maximum change over time			50mS  Zero voltage sensing to minimise EMI/RFI

Operating Voltage range			240VAC version (216VAC to 264VAC)

120VAC version (90VAC to 132VAC)

Operating temperature range			-20 deg C to +75 deg C

Maximum Voltage present on unpowered  inlet	L-N = 0.5 VAC @ 0.25mA

N-E = 8VAC @ 3.33mA

L-E = 8VAC @ 3.33mA

Maximum load (power switch version)		16A RMS

Maximum load (no power switch version)	16A RMS

Residual Earth current 				Zero mA (with no equipment connected to outlets)

Inlet filtering					100nF Capacitor, X2 rated EN132400 per inlet

Outlet filtering					1 x 100nF Capacitor, X2 rated EN132400

Depth including tie bar				395mm approx

Depth excluding tie bar				300mm approx.

Width						438mm (19 Inch)

Height						44.5mm (1U Rack-mount)

Weight						3.7Kg approx.

### Performance

The switch over circuit has been tested whilst connected to a PC with programs running with no adverse effects even with multiple change-overs within short succession.

### Future Development Program:

It is our intention to offer the Auto Switch facility on the following versions:

- Standard, single power switch MDU

- Sequence start MDU

- Network controlled MDU

- As a stand-alone version to enable Auto Switch upgrades to existing installations.

One-4-Power Ltd.

No. 2 Sorrel Close

Burghfield Common

Reading

Berkshire

RG7 3YS

Tel: 0118 9835498

FAX: 0118 9835498

www.one4power.co.uk

email: sales@one4power.co.uk